##### SECTION 1000

ELECTRICAL

SECTION 1001 – ROADWAY STREET LIGHT CONSTRUCTION

1001-1  DESCRIPTION

This work shall consist of the construction of street lights and related items in accordance with these specifications and standard details at the locations and to the lines and grades shown on the plans or as directed by the ENGINEER.

1001-2  MATERIALS

1001-2.1  General.  Materials to be furnished by the CONTRACTOR shall be all materials required to install roadway street lighting in place as shown on the plans complete and ready for operation.

All materials and equipment furnished shall be new and shall be approved by the Underwriter's Laboratories, Inc. as conforming to its standards in every case where such a standard has been established for the particular item in question.

It is the intent of the plans and specifications to comply in every respect to the requirements set forth by the National Electric Code, the North Dakota State Electrical Board, the local utility company, and the ordinances established by the City, and it shall be the responsibility of the CONTRACTOR to ensure that the above requirements are met in every respect.

Should any requirement of the above not be complied with by the plans or the specifications either through omission of equipment, material, and method of installation, or by specification of material, equipment, or installation methods, the CONTRACTOR shall immediately notify the ENGINEER.

Where items of equipment and/or materials are specifically identified herein by a manufacturer's name, model, or catalog number, only such specific items may be used in the base bid.  If the CONTRACTOR desires to use items of material and equipment other than that named in the base bid, CONTRACTOR or supplier shall apply in writing to the ENGINEER for approval of substitution at least 7 days prior to opening of bid.  Request shall be in duplicate.  Submittals must indicate the specific item or items to be furnished in lieu of those specified together with complete technical data and comparative data on specified items and proposed items.

All approved substitute items will be clearly identified in an addendum which will be sent to all bidders well in advance of opening of bids.  Only those items on the drawings and specifications and those items approved prior to bidding shall be furnished and installed on this project.

Where substitute items are used, the CONTRACTOR shall assume all responsibility for physical dimensions and pay for all changes resulting from substitutions.  This responsibility shall also include all extra work necessitated by other trades as a result of the substitutions.

The CONTRACTOR shall submit shop drawings or product data, in accordance with Section 135, covering the following items:

1.  Feed point enclosures, relays, switches, panels, and photo cells.

2.  Cable.

3.  Conduit.

4.  Light standard poles, each type.

5.  Luminaires, each type.

6.  Junction boxes.

7.  Splice connectors.

Drawings or product data shall be marked as to item designation and submitted within 30 days after contract awards.  No equipment shall be ordered until drawings and product data have been approved by the ENGINEER.

Submit shop drawings to:

City of Watford City

Engineering Department

213 2nd Street NE

P.O. Box 494

Watford City, ND 58854-0494

The CITY reserves the right to order additional light standards and/or luminaires along with the CONTRACTOR's shipment for the specific project for the following types of Light Units B, B1, BR, C, C1, D1, and D2, as detailed in these specifications.  Materials are to be billed to the CITY at the CONTRACTOR's invoice cost plus 15 percent.  The CITY will be responsible for unloading and storing additional materials ordered by the CITY.  The CONTRACTOR shall contact the CITY, by letter, prior to placing the CONTRACTOR's order for light standards and luminaires.  The CITY shall state quantities of additional materials, per item desired, in a letter addressed to the CONTRACTOR.

The CONTRACTOR shall keep one set of plans with him at all times to red line locations of conduits not requested by the CITY, but installed by the CONTRACTOR for his convenience.  In addition, the red lined drawings shall contain relocation of light standards, feed points, and changes in the cable location.  This red lined plan set shall be turned over to the CITY prior to the close of the project.

The contractor shall be responsible for locating and marking all underground circuits associated with this project throughout the course of the project.  The contractor shall be relieved of this responsibility at such point in the project when the lights are fully operational and a set of red lined drawings have been submitted and approved by the ENGINEER.  The cost for all locating and marking shall be incidental to the cost of the project.

1001-2.2  UNDERGROUND CABLE AND CONDUCTORS.  Underground circuit conductors shall be stranded copper, Type “RHH/RHW” or "USE," conductors insulated for direct burial and rated 600 volts.  Conductor sheath shall be marked as to voltage, AWG, Type (RHH/RHW-USE), and manufacturer.  The conductor sheath shall be color coded to indicate red-power, blue-power, and white-neutral.

Underground ground conductor shall be No. 6 stranded bare copper or Type TW insulated copper ground conductor.  Service conductors from electric utility service point shall be Type RHW-USE, sized as per utility company requirements and electrical loading.

1001-2.3  CONDUITS.  Conduits shall be 2-inch steel rigid galvanized conduit when jacked in place with bushings at each end.  When pulled into place or direct buried, conduits shall be 2-inch polyvinyl chloride (PVC) schedule 40, U.L. listed for electrical usage and sunlight resistant.  Bell type fittings shall be placed at both ends.

1001-2.4  MARKER TAPE.  Marker tape shall be 6-inch wide red plastic tape marked "Caution - Buried Electric Cable."

1001-2.5  JUNCTION BOXES.  Junction boxes shall be made of a lightweight, high-density polymer concrete composite, UL listed with knockouts for cable entrance.  The box shall comply with ANSI/SCTE 77 with a design load of 22,500 pounds, a test load of 33,750 pounds, and meet ANSI Tier 22 test provisions.  The cover shall meet an 8,000 pounds design load and 12,000 pounds test load.  Boxes shall be resistant to sunlight exposure, weathering, chemicals, and unaffected by freeze-thaw cycles to

-50(F.  Minimum dimensions shall be 24” X 13” X 18”D with stackable boxes or extensions allowed to achieve required depth.  Box covers shall have stainless steel hex bolts and be stamped with standard logo "Street Lighting."

Box manufacturer shall be Quazite, model PG, Oldcastle Precast, Inc., model  Synertech Heavy-Duty, or approved equivalent.

1001-2.6  SPLICE CONNECTORS.  Splice connectors at junction boxes for multiple connections shall be Homac, Type RAB-X-URD-BUSS submersible insulated subsurface terminal for copper conductor, or approved equivalent.

Splice connectors at pole hand hole shall be Penn-Union PBNA2/0X,or approved equivalent.

1001-2.7  FEED POINT ENCLOSURE

(a)  Pad mounted feed point enclosure shall be made of minimum 1/8-inch aluminum, with a brushed aluminum finish, rated for NEMA 3R and be ETL or UL listed in accordance with UL 50 . Dimensions of the enclosure shall be 42”W X 12”D X 51”H and shall have a domed roof with a NEMA 3R drip shield and two doors. The doors shall have an aluminum continuous piano-style hinge, a neoprene gasket, and a stainless steel 3-point latch capable of being padlocked.  The enclosure shall be equipped with back panel rails such that equipment may be mounted in the cabinet with no penetrations to the exterior of the cabinet.  The back panel shall be galvanized steel.  All hardware shall be non-corrosive.

The enclosure shall be manufactured by Povolny Specialties, or approved equivalent.

(b)  Pole mounted feed point enclosure shall be made of minimum 1/8-inch aluminum, with a brushed aluminum finish, rated for NEMA 3R and be ETL or UL listed in accordance with UL 50.  Dimensions of the enclosure shall be 30”W X 8”D X 36”H, with an exterior mounting plate and a single door. The door shall have a minimum of three lift off hinges, a neoprene gasket, and a stainless steel 3-point latch capable of being padlocked.  The enclosure shall be equipped with back panel rails such that equipment may be mounted in the cabinet with no penetrations to exterior of the cabinet.  The back panel shall be galvanized steel.  All hardware shall be non-corrosive.

The enclosure shall be manufactured by Povolny Specialties, Hoffman, or approved equivalent.

1001-2.8  RELAYS, PANELS, SWITCHES, PHOTO CELL

(a)  Relays shall be RCOC Type MR-UD No. 6342 with normally open contacts.

(b)  Electric panel shall be single-phase load center with enclosure rated NEMA 1 with minimum 12 spaces/24 circuits, rated 120/240 volt, 100-amp two-pole main breaker, copper bus, and a minimum 22,000 amp IR. The load center shall be Square D, model QO120M100, or approved equivalent.

(c)  A single pole test switch shall be provided to tests the lights.  The switch shall be mounted on a metal box with raised switch cover.  Utilizing laminate engraved nameplate(s), the switch options shall be marked as “Test” and “Auto” with two (2) 1/2-inch by 1½-inch nameplate.  Marker as a means of labeling will not be acceptable.

(d)  Photo cell for control of relays shall be Hubbell PBT-1, or equal.

1001-2.9  STREET LIGHT STANDARDS

(a)  Type B, B1 Standards shall be pre-stressed spun concrete of natural polished finish the precast type as manufactured by Ameron MEO-8.5-C6 Brace - No. 112 - sky gray, natural polished finish or equal to provide a minimum mounting height of 28 feet.  Poles shall be complete with hand holes and metal covers secured in place with screws.  Concrete light standards shall be equipped with a grounding lead to bond the pole to the grounding system.

(b)  Type BR standards shall be pre-stressed spun concrete of the precast type.  Poles shall be Ameron SEO-4 (direct-embedded octagonal) with a 2 7/8-inch o.d. cast aluminum top tenon to provide a minimum mounting height of 13 feet.  Color shall be No. 112 - sky gray, natural polished finish.  Poles shall be complete with hand hole access and covers secured in place with screws.  Concrete light standards shall be equipped with a grounding lead to bond the pole to the grounding system.

(c)  Steel light standards (C, C1) shall be steel, galvanized type, as manufactured by Millerbernd RLDA6-400ND, Valmont Industries, Inc. DS90 or equal, of one- or two-piece construction.  Galvanizing shall be in accordance with ASTM A123.  The shaft shall have only one longitudinal weld and shall have a minimum yield strength of 50,000 psi.

The Davit type mast arm shall be constructed of same material and by same method as the shaft.  Mast arm shall have a tenon adaptor for luminaire mounting.

The anchor shall be a one-piece steel casting secured to the lower end of the shaft by two continuous welds.  One weld shall be inside the base at the bottom of the shaft and the other shall be on the outside of the shaft at the top of the anchor base.  The welded connection shall develop the full strength of the adjacent shaft section.  The anchor base shall be complete with bolts, washers, shims, and bolt covers with cap screws for attaching covers to base.  The grounding lug shall be provided inside of the hand hole.

(d)  Type D1 and D2 Standards shall be pre-stressed spun concrete with a black exposed aggregate finish with a gloss acrylic coating (6P3A) as manufactured by Ameron MEO-6 to provide a minimum mounting height of 19.5 feet.  Poles shall be complete with hand holes and covers, painted to match pole color, and secured in place with screws.  Concrete light standards shall be equipped with a grounding lead used to bond the pole to the grounding system.

A hand hole shall be provided in the shaft opposite the roadside of the pole for all pole types unless otherwise noted in the plans.  Hand holes shall be a minimum of 4 inches by 6 inches with reinforced frame and removable metal cover, and the cover shall be secured in place with screws.

1001-2.10  LUMINAIRES, LAMPS, BALLAST, POST WIRING WITH FUSE

(a)  Luminaires for the Types B/B1 or C/C1 shall be totally enclosed with integral high-pressure sodium.  Luminaires shall consist of head with ballast, socket, and optical assembly.

Heads shall have a die-cast aluminum housing. The housing shall have a drop down power door with no photocell receptacle and be designed for internal wiring and an internal 4-bolt 2-inch slip fitter adjustable plus or minus 5 degrees ((5() from horizontal.

An anodized aluminum reflector with a drop glass prismatic refractor shall provide a uniform distribution, IES Type III, medium, semi cutoff distribution unless otherwise noted in the plans or specifications.  Photometric data shall be provided.

Ballasts shall be a constant wattage autotransformer or peak lead autotransformer with multiple voltage taps and suitable for cold weather starting at an ambient temperature of -20(F.  Data listing starting and normal operating currents shall be provided. Luminaire shall have an encapsulated starter.

Lamps shall supply the following:

150 watt - 13,800 Lumens, Mean

250 watt - 25,000 Lumens, Mean

400 watt - 45,000 Lumens, Mean

Type B luminaires shall be as follows:  American Electric Lighting, Model 315-15S-CA-MT1-R3DG-4B-ULNREC, General Electric, Model MDRA-155-0-A1-2-R-MS3-2U, or approved equivalent.

Type B1 and Type C luminaires shall be as follows:  American Electric Lighting, Model 325-25S-CA-MT1-R3DG-ULNREC, General Electric, Model MDRA-25S-0-A-1-R-MS3-2U, or approved equivalent.

Type C1 luminaires shall be as follows:  American Electric Lighting, Model 325-40S-CA-MT1-R3DG-ULNREC, General Electric, Model MDRA-40S-0-A-1-R-MS3-2U, or approved equivalent.

All Luminaires, by type specified, shall be by one manufacturer similar and equal.

(b)  Luminaires for the Type BR lights shall be Holophane PTU-15AHP-MA-B-G3-B series post-top units, non-photocell type with multiple voltage/high power factor ballasts, 150 watt and IES Type III medium, semi cutoff distribution glass refractor.  Luminaires shall be equipped with integral slip fitter for 3-inch O.D. tenon mount.

(c)  Luminaires for the Type D1 lights shall be Holophane ST-15AHP-MA-B3B series post-top units complete with ornate trim including spike finial, bands, ribs, and medallions, black in color.  Luminaires shall be non-photocell type with high power factor ballasts, 150 watt, and IES Type III medium, semi cutoff distribution glass refractor.  Luminaires shall be equipped with integral slip fitter for 3-inch O.D. tenon mount.

(d)  Luminaires for Type D2 shall be Whatley Lighting, model 1542TR-150HPS-MT-HR3-BLK with a Type PT01 mounting arm.  The luminaire shall be non-photocell type with high power factor ballast (multi-tap wired for 120V), 150W HPS, IES Type III optics, and sandblasted-tempered glass globe.  The mounting arm shall have a slip fitter for 3-inch O.D. tenon mount.  The fixture and arm shall be cast aluminum and shall have a polyester powder coat finish.  All hardware shall be stainless steel.

(e)  Post wiring shall be No. 10 AWG stranded copper, Type THHN/THWN 600-volt cable, three conductors minimum (power, neutral and ground).  Post wiring fuses shall be a Type FNM 10 ampere fuse with a Buss Type HEB in line fuse holder.

1001-2.11  WOOD POLE.  Wood pole shall be 30 feet Class 3 full length pressure treated (PENTA) pole.

1001-2.12  UNDERGROUND SPLICES.  Underground splices shall not be permitted unless approved by the CITY.  No more than two underground splices shall be permitted on any continuous run of cable between feed points, poles, and junction boxes.

When the ENGINEER has determined that a splice is acceptable, the CONTRACTOR shall install a Homac, Type FSS splice.  The splice shall then be wrapped once with 3M tape, Type 130C and twice with Scotch tape, Type Super 33 Plus.

1001-3  CONSTRUCTION REQUIREMENTS

1001-3.1  FEEDER AND DISTRIBUTION CIRCUITS.  All feeders and distribution circuits shall be of the multiple type, 120/240 volt, single phase, and shall consist of two or three conductors constituting one or two 120-volt circuits or a single 240-volt circuit.  Plans shall indicate where three-wire circuits (2-120) volt and two-wire circuits (1-120 volt or 1-240 volt) are to be installed.

The system shall be laid out on the plans, and distribution circuits shall be routed as shown.

Individual lamp circuits are shall be fused in the base of each lighting standard.  Tape fuse kits with a 1/2-inch lapped layer for a distance of 1½ inches on each side of joint with conductor.  Fuse holders to be complete with proper fuse to protect luminaire ballast.  The neutral conductor shall be solidly connected, unfused, throughout system.

Ground conductors shall be provided between all metal poles and associated feed points.  Bond to metal pole, to ground rod in pole base, feed point enclosure, feed point panels, relay cabinets, and ground rod.

Conductors shall be continuous from pole base to pole base or from feed point to pole base.  Splicing conductors underground will not be allowed without specific approval of ENGINEER.

1001-3.2  CABLE INSTALLATION:  IN TRENCH AND/OR CONDUIT.  Distribution circuits consisting of conductor cables, quantity and size as designated on plans and installed direct burial in trench or in conduit, shall be installed to a depth of not less than 24 inches below finished grade.  Under streets, driveways, and sidewalks, all conductors shall be installed in conduit, and the top of the conduit shall be not less than 24 inches below the top of concrete, asphalt, or hard surfacing.

Conductor cables shall be packed in sand to provide a cushion and to facilitate drainage in the following manners:  Excavate trench to required minimum depth of 27 inches (exception of 48 inches from feed points to transformers, in easements, or as specified).  Trench shall be filled with 3 inches of clean, washed sand bedding, leveled, and lightly tamped.  Conductor cables, quantity, and size designated on plan shall be laid loosely in trench and spaced as per drawing detail.  Conductor crossovers shall be avoided.  Contractor may be required to utilize a paddle template ahead of the 3 inches of sand cover to insure proper spacing.  Cover sand shall not be less than 3 inches in depth over conductors.  Sand shall again be leveled and lightly tamped the full width of the excavated trench.  Trench shall then be backfilled and tamped in regular manner.

If a specific excavation is judged to be free of rocks and debris, CONTRACTOR shall be allowed to utilize backfill without sand cushion upon approval of the ENGINEER.

Care shall be taken during installation of conductors to not bend or kink cable to a radius of less than six times the cable diameter.

On conductors installed on branch circuit feeders routed underground from pole to pole, all circuits shall be brought up into pole for splicing (especially lights on alternated circuits) unless indicated on plans.  No splicing will be allowed of underground cable.  Splicing will only be allowed in junction boxes, pole bases, or feed point cabinets.  Split bolts may NOT be used as a means of splicing or bonding.

Conduit shall be provided under hard surfaced driveways, streets, and alleys and when rising up into feed points.  Conduit not installed direct burial underground shall be jacked or bored.  Rigid steel galvanized conduits shall be installed when jacked or heavy wall Schedule 40, UL Listed PVC may be utilized when installed with a directional bore or "mole" device.  All conduits shall extend a minimum of 12 inches beyond each roadway, alley, driveway, or concrete surface, but not more than 18 inches or as directed by the ENGINEER.  Rigid steel conduit ends shall be carefully reamed to provide a smooth surface for conductors.  Plastic bushings shall be placed on rigid steel conduit ends, and PVC conduit ends shall be terminated with bell type fittings.  All cable run through conduit shall be pulled by hand and shall not be strained in any manner.  A slack loop shall be provided in conductors prior to entering any conduit.  All conduit installed, whether direct buried, bored, or jacked, shall be a minimum of 24 inches below finished grade.  Where practical, conduit shall be sloped to provide drainage.  Two-inch PVC conduit shall be provided for the risers at the pad mounted feed points and 2-inch rigid steel galvanized at pole mounted feed points.

If an obstruction is encountered when "jacking" or boring conduit under a concrete or asphalt street, driveway, or alley, or for any reason it becomes impractical to install the conduit in this manner, the ENGINEER may grant the CONTRACTOR permission to cut or saw the street, drive, or sidewalk so conduit can be trenched into place.  The width of the concrete or asphalt to be removed and the depth of the saw cutting shall be performed as directed by the ENGINEER.  No extra payment will be made for cutting, removing, and replacing the concrete or asphalt.  Cost of installing conduit by this method shall be included in the price for 2-inch conduit jacked or pulled in place.  Street "cuts" shall not be started until permission is granted by the ENGINEER in writing.

Any excavations or exploratory cuts to any asphalt or concrete surface for the purpose of locating any existing underground utilities or obstructions to aid in the boring or jacking of conduit shall be included in the price bid for 2-inch conduit jacked or pulled in place including any traffic control requirements.  No extra payment will be made for sawing, removing, and replacing the concrete or asphalt.  The width of the concrete or asphalt to be removed and the depth of the saw cutting shall be performed as directed by the ENGINEER.

In lieu of trenching to install either conductor or conduit, the CONTRACTOR may utilize directional boring.  In this event, alignment and depth shall be maintained according to plan.  Any deviation in alignment and/or depth shall be corrected by the CONTRACTOR as directed by the ENGINEER, at no cost to the CITY.  CONTRACTOR shall be paid as if trenched by the appropriate unit price bid for 27-inch trenching plus the unit price bid for sod (conversion from square yards to linear feet shall be: 1 square yard equals 6 linear feet).  Any conduit bored solely for the CONTRACTOR's convenience and/or not paid for at the unit price bid for jacked or bored conduit shall be the CONTRACTOR's expense, at the discretion of the ENGINEER, for those locations with existing grassed vegetation. The CONTRACTOR shall also be paid for the relocation of any mailbox without a concrete base that would have been relocated if the cable or conduit would have been installed by trenching.  For mailboxes with concrete bases, the CONTRACTOR shall be paid for 2-inch conduit jacked or pulled in place beneath the concrete base.

Where excavations for cables or conduits are made, the backfill shall be compacted in 4-inch lifts or layers.  Only suitable material as defined by Section 202-1c shall be used for backfill of trenches.  Backfill with sub-standard material is prohibited even though such materials may have been excavated from the trench.

Excavated trenches shall be compacted by approved methods to 95 percent of maximum dry density at optimum moisture in accordance with ASTM D1557 when under future pavement or concrete areas.  Boulevards, grassed areas, and any other disturbed areas shall be compacted to 90 percent of maximum dry density at optimum moisture.

Any tree roots encountered and/or damaged during trenching or boring shall be handled according to Subsection 201-2.4 "Tree Root Cutting."

Marker tape shall be provided near the top of trench (6 inches below final grade) in all trenches.  Cost shall be incidental to the trenching price.

1001-3.3  JUNCTION BOX INSTALLATION.  Junction boxes shall be provided at locations shown on plans installed in the boulevard.  Top of junction boxes shall be the same elevation as top of adjacent curb or sidewalk.  Provide a 12-inch base of crushed rock or gravel as shown in standard detail.

Provide slack loop in all conductors so conductor can be pulled up out of junction box to a minimum of 24 inches above ground.

Splice connectors shall be as indicated in Subsection 1001-2.6 “Splice Connectors” and shall be raised off the bottom of the junction box such that they are directly below the junction box cover and positioned upward.

Tape connector kits with half lapped layer of rubber or synthetic rubber tape and one layer of tape for a distance of 1½ inches each side of joint.

1001-3.4  STREET LIGHT FEED POINTS.  Street light feed points consist of pole mounted, pad mounted, and modifications and additions to existing.

(a)  Pad Mounted (New).  See detail drawing for typical details.  New pad mounted feed points shall be set on a concrete pad which is set on a 12-inch thickness of a crushed rock subbase.  Provide 1-inch chamfer all around and down vertical sides to a minimum of 2 inches below grade.

Concrete pad shall be 52 inches long by 24 inches wide by 12 inches deep (52"L x 24"W x 12"D) and shall be constructed in accordance with Section 500 for Concrete Construction.  Provide seven (7) 2-inch PVC stub outs down through concrete base and a minimum of 12 inches beyond edge of base.  Point one (1) conduit towards power company transformer and six (6) towards direction of outgoing circuits.  Provide two 1-inch conduits for ground rods through the base only.  Notify ENGINEER a minimum of 24 hours prior to pouring concrete base such that the form and cable entrance may be inspected.

Provide unistrut mounting brackets and a galvanized steel back panel.

Provide 40 amp two-pole breakers for each pair of 120-volt street light circuits that share a neutral conductor and a 15-amp one-pole breaker for control circuit, 20-amp one-pole breaker for convenience outlet.  Paint handle of 15-amp breaker red.

Provide one (1) relay for each three (3) wire street light circuit (2-120V) or one (1) relay for each two (2) wire street light circuit (1-240V).

Install switch to be connected into control circuit to bypass photocell for daytime test of street lights.

Install G.F.I. outlet.

Provide two 5/8-inch by 10-foot copper ground rods in two conduits through concrete to below cabinet.  The two ground rods shall be a minimum of 6 feet apart and shall be looped.  Bond all circuits, relay cabinets, electric panel cabinet, enclosure, and neutral.

Photo cell shall be mounted on side of enclosure as shown on detail.  Direct photo cell to north.

Provide 120/240-volt single-phase service from power company.  Pad mount transformer.  Service shall be installed in 2-inch, minimum, conduit with three (3) Type RHW-USE conductors.  Underground service lateral for the feed point shall be 36 inches deep and shall be included in the cost of the feed point.  All utilized conduits shall be sealed at duct plug as manufactured by Tyco, Series JM.  Route conduit entrance through meter.  All unfused conductors within the feed point enclosure shall be placed in conduit.

Location of pad mounted feed points as shown on plans shall be determined by location of power company pad mount transformer and by power company space requirements.  CONTRACTOR shall verify location of power company pad mounted transformer.

(b)  Pole Mounted (New).  Incoming service shall be fed from below grade unless otherwise shown on the plans.  Provide 1½-inch steel galvanized conduit, minimum, and three (3) THW conductors.  Route conduit entrance through meter.  All unfused conductors within the feed point enclosure shall be placed in conduit.

Provide two (2) 5/8-inch by 10-foot copper ground rod at bottom of pole as shown on detail and ground enclosure and service.  The two ground rods shall be a minimum of

6 feet apart and shall be looped. Bond all circuits, relay cabinets, electric panel cabinet, enclosure, and neutral.

Provide one (1) relay for each three (3) wire street light circuit (2-120V) or one (1) relay for each two (2) wire street light circuit (1-240V).

Feed points mounted on poles belonging to others shall conform to all requirements of the pole's owner, such as use of standoff brackets.  The CONTRACTOR shall be responsible for coordinating with the pole's owner in conforming to their requirements. CONTRACTOR shall verify location of power company pad mounted transformer.

(c)  Pole or Pad Mounted: (Existing) Additions and Modifications.  Provide additional relays and feeder conduits as shown or specified.  Relays to match existing.

If cabinet is painted, paint entire exterior portion of each existing feed point associated with this project as follows:

1.  Wire brush entire surface and sand with extra fine sandpaper.

2.  Wipe down with thinner.

3.  Brush or spray on two (2) coats of ZRC zinc dust primer.

4.  Brush or spray two (2) coats of enamel paint, dark green, suitable for exterior use.

1001-3.5  STREET LIGHT STANDARD WITH CONCRETE FOUNDATIONS AND DIRECT BURIED

Street light standards shall be set as shown on the plans with the hand hole facing away from curb and cable entrances parallel to roadway.  Install 1/2-inch by 10-foot ground rod at each street light.  All street light standards shall be grounded.  Bond ground conductor, street light standard, and ground rod.

The conductor leads to the luminaire (power, neutral and ground) shall extend from the cable in the light standard base through a fuse holder with a fuse.  The fuse holder shall be supported by the conductors at the level of the hand hole.  Sufficient excess conductor length shall be provided to permit withdrawal of the fuse holder through the hand hole a minimum of 6 inches outside of the hand hole for purposes of installation and inspection.  The neutral wire shall not be fused.

Luminaires shall be adjusted to supply light to roadway as directed by the ENGINEER.

The concrete to be used in the construction of the concrete housekeeping pads, base pads, and foundations shall be a minimum of 3500 psi strength at 28 days with a minimum of six (6) bags of cement per cubic yard of concrete and shall conform in all respects to the CITY Specifications, Section 600 for Sidewalks, Driveways, Curb, and Combined Curb and Gutter.

(a)  Direct Buried Light Standards.  A concrete housekeeping pad of dimensions shown in the standard detail shall be constructed around the base of the direct buried concrete standard.  A concrete-bearing base pad 6 inches thick, minimum,  shall be provided under the bottom of the pole as shown.  Provide roofing tar paper around poles between pole and concrete pad.  In sidewalks, provide 3/4-inch expansion joint around concrete pad between concrete pad and sidewalk.

All costs of constructing the concrete pads and bases shall be included in the price bid for furnishing and installing concrete street light units.

(b)  Light Standards with Concrete Foundations.  Concrete foundations shall be installed as per standard detail.  Foundations shall be completed with anchor bolts, rebar, and conduit stub-in. Anchor bolt spacing to accommodate poles shall be verified in the field prior to construction.  The CONTRACTOR shall notify the ENGINEER at least 24 hours prior to pouring a concrete foundation such that the form with the anchor bolt placement, rebar, conduit stub-ins, and ground rod can be inspected.  The CONTRACTOR shall provide concrete tests in conformance with CITY Specifications, a minimum of one (1) test per day or a minimum of one (1) test per five (5) light standard foundations or as directed by the ENGINEER.

1001-3.6  REPAIRS TO SIDEWALKS AND STREETS.  In locations where sidewalks, pavement, driveways, or streets are opened for installation of cable, conduit, or poles, the removed area shall be replaced to the original thickness.  The repair shall conform in every way to either Sections 300 and 400 for AC Pavement or Section 500 for Concrete Repair.

In the event of the inability of the CONTRACTOR to either jack or bore conduit or cable under an improved area, the CONTRACTOR shall, with the ENGINEER's permission, be allowed to open cut the area.  The CONTRACTOR shall minimize the area removed as much as possible but must allow enough area to allow for installation of cable or conduit and access for compactive equipment.  The CONTRACTOR shall make cuts so that uniform edges for trenches may be obtained.  In concrete, the CONTRACTOR shall utilize existing joints or sawed joints as required.

The backfill under all improved areas shall be Class A and shall be compacted to not less than 90 percent of maximum dry density at optimum moisture in accordance with ASTM D1557.

Where specified on plans, CONTRACTOR shall be paid at the unit price bid for Concrete or AC Pavement unless incidental.  In the event of the inability of the CONTRACTOR to jack or bore under an improved area and an open cut is required, the CONTRACTOR shall be paid at the unit price bid for installed material only.  Repair shall be at CONTRACTOR's expense.

In the event of damage of an improved area due to construction, all repair costs shall be borne solely by the CONTRACTOR.

All AC Pavement patches or repairs shall be seal coated in accordance with Section 400 "Flexible Surface Courses."

1001-3.7  SODDING.  Sodding installation and care shall conform in every respect with Section 1203 of the CITY Specifications with the following exception:  Existing sod may be cleanly cut, removed, rolled up, kept moist, replaced, and paid per square foot of sodding.  CONTRACTOR shall then be responsible for care as per CITY Specifications. Topsoil to a minimum depth of 4 inches shall be salvaged and replaced or provided and added to the top of the trench incidental to sodding bid item.

1001-3.8  MAIL BOXES - REMOVE AND RESET.  In some areas mail boxes are already in place behind the curb and will require removal and replacement to make way for trenching operations.

CONTRACTOR shall be responsible for:

1.  Removal and replacement of mailboxes and shall make every effort to remove and replace in the same day.  In the event this is not possible, CONTRACTOR shall construct a temporary wood base to hold mailboxes upright.

2.  Coordination with Watford City Post Office.  The Post Office shall be informed when a mailbox is removed and not replaced for more than 24 hours to coordinate mail delivery.

Mailboxes shall be reinstalled with the front of box directly above the box side (property side) of the curb with the bottom of the box 38 inches above the top of curb.  Boxes shall be plumb, level, set square with street, and tamped solidly in place.

Mailboxes installed on concrete pads and metal pedestals shall not be removed.  A conduit shall be installed under the base as directed by the ENGINEER.

1001-3.9  NAMEPLATES.  The CONTRACTOR shall provide nameplates per standard detail for all feed point cabinets.  The nameplate shall consist of letters and/or numbers, printed on a thermosetting laminated plastic consisting of melamine or phenolic core and melamine surface.

The nameplates shall be mounted on the front of the feed point or control cabinet door with a combination of aluminum round head screws and Minnesota Mining and Manufacturing Company adhesive similar to Type EC-847.

Nameplates to have a black background with white letters and/or numbers unless noted otherwise.  One (1) 1½-inch by 6-inch nameplate and one (1) 1½-inch by 3-inch nameplate shall be provided for each new feed point and two (2) 1/2-inch by 1½-inch nameplates for each test switch.  The feed point number and location shall be as designated on plans.

1001-3.10  REMOVAL OF STREET LIGHT STANDARDS.  The standards shall be removed from the sites shown on the plans, salvaged, transported, and stored (by blocking and supporting at three points) in the CITY storage yard located at the Municipal Solid Waste Facility on North 52nd Street.  The luminaire receptacle wires shall be disconnected at the fuses and the luminaire shall be removed from the mast arm, salvaged, and delivered to CITY stores at 601 South 26th Street.  Where the plans call for salvaging the conductors in place and resplicing these conductors, the standards shall be removed carefully to prevent damage to the conductors.  Splices shall be made by using approved materials.  The hole where the standard was removed shall be filled with earth supplied by the CONTRACTOR and tamped to the density of the surrounding soil.

1001-3.11  RELOCATE STREET LIGHT POLE.  This item shall consist of removing a light standard from its present location and installing at a new location shown on the plans and connecting to the new or existing street light system wiring.  The CONTRACTOR shall furnish any materials and equipment required for removing and replacing the street light pole.  Installation shall be performed in accordance with these specifications.

1001-3.12  TESTS.  When the installation is complete and at such time as may be specified by the ENGINEER, the CONTRACTOR shall conduct an operating test for approval.  The equipment shall be demonstrated to operate in accordance with the requirement of the specifications, the plans, and to the satisfaction of the ENGINEER.  The CONTRACTOR shall furnish all instruments and personnel required for all tests.  All test results shall be recorded.  The CONTRACTOR shall be present during all tests and inspections unless so informed by the ENGINEER.  Nighttime tests and inspections may be held at the option of the ENGINEER.

1001-4  MEASUREMENT AND PAYMENT

1001-4.1  TYPE B STREET LIGHT UNITS (150 Watt HPS).  Type B Street Light Units consist of:

- Designated luminaire with ballast and lamp.

- Concrete direct buried poles with bracket.

- Wiring and connections to underground circuits.

- Ground rod with connections.

- Fuse holder and fuses.

- Concrete pads.

- Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.2  TYPE B1 STREET LIGHT UNITS (250 Watt HPS).  Type B1 Street Light Units consist of:

- Designated luminaire with ballast and lamp.

- Concrete direct buried poles with bracket.

- Wiring and connections to underground circuits.

- Ground rod with connections.

- Fuse holder and fuses.

- Concrete pads.

- Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.3  TYPE C STREET LIGHT UNITS (250 Watt HPS).  Type C Street Light Units consist of:

1.  Designated luminaire with ballast and lamp.

2.  Galvanized steel, bolt down, base type pole with bracket.

3.  Wiring and connections to underground circuits.

4.  Fuse holder and fuses.

5.  Reinforced concrete base, anchor bolts, anchor bolt covers, ground rod, and conduit.

6.  Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.4  TYPE C1 STREET LIGHT UNITS (400 Watt HPS).  Type C1 Street Light Units consist of:

1.  Designated luminaire with ballast and lamp.

2.  Galvanized steel bolt over base type pole with bracket.

3.  Wiring and connections to underground circuits.

4.  Fuse holder and fuses.

5.  Reinforced concrete base, anchor bolts, anchor bolt covers, reinforced ground rod, and conduit.

6.  Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.5  TYPE BR STREET LIGHT UNITS (150 WATT HPS).  Type BR Street Light Units consist of:

- Designated luminaire with ballast and lamp.

- Concrete direct buried poles.

- Wiring and connections to underground circuits.

- Ground rod with connection.

- Fuse holder and fuses.

- Concrete base and housekeeping pad.

- Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.6  TYPE D1 STREET LIGHT UNITS (150 WATT HPS).  Type D1 Street Light Units consist of:

- Designated luminaire with ballast and lamp.

- Concrete direct buried poles.

- Wiring and connections to underground circuits.

- Ground rod with connection.

- Fuse holders and fuses.

- Concrete base and housekeeping pads.

- Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.7  TYPE D2 STREET LIGHT UNITS (150 WATT HPS).  Type D2 Street Light Units consist of:

- Designated luminaire with ballast and lamp.

- Concrete direct buried poles and mounting arm.

- Wiring and connections to underground circuits.

- Ground rod with connections.

- Fuse holders and fuses.

- Concrete base and housekeeping pads.

- Unit set in place and ready for operation.

Measurement for payment shall be on a per each (EA) unit basis for each complete unit installed and ready for operation.

1001-4.10  TWO-INCH CONDUIT "JACKED" OR PULLED IN PLACE

(1)  Two-inch conduit jacked in place shall be 2-inch steel rigid galvanized conduit, jacked in place at proper depth sloped for drainage complete with bushings each end and extending 12 inches beyond each side of roadway, drive, or walk or 2-inch PVC (Schedule 40) pulled in placed by use of direct bore or drill.  PVC shall be sloped similar to 2-inch rigid.

(2)  Excavations required for "setting up" for pushing or drilling conduit shall be a part of the conduit installation price.  This includes breaking out and replacing concrete, asphalt, excavations, filling and tamping, and replacement of grass or sod.

Measurement for payment shall be for each linear foot (LF) of conduit installed and approved by the ENGINEER.

1001-4.11  TWO-INCH CONDUIT - PVC LAID IN TRENCH.  Two-inch conduit, PVC Laid in Trench shall include conduit laid in a trench free of voids and rocks, sloped for drainage and properly backfilled as per specifications.  Trenching cost is part of Subsection 1001-4.12 "Trenching - 27-Inch Depth."

Measurement for payment shall be for each linear foot (LF) of conduit installed and approved by the ENGINEER.

1001-4.12  TRENCHING - 27-INCH DEPTH.  Trenching shall include all excavation required for conductor trenches, sand cushion, backfill, tamping, and marker tape.

Measurement for payment shall be for each linear foot (LF) of trench excavated, backfilled, tamped, and with surface restored to original conditions all as accepted and approved by the ENGINEER.

1001-4.20  JUNCTION BOXES.  Junction boxes shall include all splice connectors, excavated, backfilled, tamped, and with surface restored to original conditions.

Measurement for payment will be for each (EA) junction box installed complete and accepted by the ENGINEER.

1001-4.21 and 1001-4.22  COPPER CIRCUIT CONDUCTORS.  Three (3) No. 4 or two (2) No. 4 stranded copper, as the case may be, Type RHW-USE single conductor - 600-volt direct burial cables laid in common trench and/or conduit shall be measured by the linear foot (LF) of three (3) No. 4 or two (2) No. 4 single conductors furnished and installed in trenches/conduits.  Measurement will be from centerline to centerline of pole or feed point.  CONTRACTOR shall make allowance for necessary conductors in and out of poles and feed point in unit price.

Payment shall be at unit price bid for each linear foot (LF) of 3- or 2-wire conductor installed and accepted by the ENGINEER.  Two-wire conductor shall be paid for under bid item 1001-4.21, and 3-wire shall be paid for under 1001-4.22.

1001-4.23 & 4.24  COPPER CIRCUIT CONDUCTORS.  Two (2) No. 2 or three (3) No. 2 stranded copper, as the case may be, Type RHW-USE single conductor - 600-volt direct burial cables laid in common trench and/or conduit shall be measured by the linear foot of two (2) No. 2 or three (3) No. 2 single conductors furnished and installed in trenches/conduits.  Measurement will be from centerline to centerline or pole or feed point.  CONTRACTOR shall make allowance for necessary conductors in and out of poles and feed point in unit price.

Payment shall be at unit price for each linear foot (LF) of 3- or 2-wire conductor installed and accepted by the ENGINEER.  Two-wire conductor shall be paid for under bid item 1001-4.23, and 3-wire shall be paid for under 1001-4.24.

1001-4.25  NO. 6 COPPER GROUND - TYPE T OR BARE.  No. 6 Copper Type TW or Bare shall include all grounding conductor, ground rods, and connections.  Ground rods (1/2 inch by 10 feet) shall be provided at all junction boxes where No. 6 groundwire is required as part of system.

Measurement for payment shall be based on each linear foot (LF) of No. 6 conductor installed, measured from junction box or pole foundation along centerline of trench or duct.

1001-4.26  MAIL BOXES - REMOVE AND RESET.  Multiple boxes on a single or double support structure shall be measured and paid for per support removed and replaced.

Payment shall be for each (EA) group removed, reset, and approved by the ENGINEER.

1001-4.27  SODDING.  Sod shall be measured and paid for under Subsection 1203-4.1.

1001-4.28  STREET LIGHT BASE.  This item consists of constructing concrete bases per those specifications and standard details for street light standards.

Street light bases shall be measured per each (EA) and paid for at the unit price bid for street light bases complete, in place, and accepted by the ENGINEER.

1001-4.29  REMOVE STREET LIGHT STANDARDS.  This item shall consist of removal, transport, and storage of street light standards.

Measurement for payment shall be per each (EA) street light standard removed and stored accepted by the ENGINEER.

    - RELOCATE STREET LIGHT POLE.  This item shall consist of removing and relocating and reconnecting conductors not to be abandoned measured per each (EA) pole in place and accepted by the ENGINEER.

1001-4.31 and 1001-4.32  COPPER CIRCUIT CONDUCTORS.  Three (3) No. 6 or two (2) No. 6 stranded copper as the case may be type RHW-USE single conductor - 600-volt direct burial cables laid in common trench and/or conduit shall be measured by the linear foot (LF) of three (3) No. 6 or two (2) No. 6 single conductors furnished and installed in trenches/conduits.  Measurement will be from centerline to centerline of pole or feed point.  CONTRACTOR shall make allowance for necessary conductors in and out of poles and feed point in unit price.

Payment shall be at unit price bid for each linear foot (LF) of three (3) or two (2) wire conductor installed and accepted by the ENGINEER.  Two (2) wire conductor shall be paid for under bid item 1001-4.31, and three (3) wire shall be paid for under 1001-4.32.